## Sheet1
Cost Estimator for digestion |  |  |  | Input
Suggestions
WAS Flowrate from Secondary Clarifiers | 500 | gpm |  | Calculation
TSS Concentration from Secondary Clarifiers | 5000 | mg/L |  | Results
Average water temperature | 70 | °F | 40-77
Converted to °C | 21.1111 | °C | 4-25
Digestion Temp | 98 | °F | 68-108
Converted to °C | 36.6667 | °C | 20-42
Electrical Usage Cost | 0.15 | $/kWh
Natural Gas Cost | 2.5 | $/MMBTU | (million BTU's)
Converted to $/kWh | 0.0085304 | $/kWh
DAF Thickened Sludge Concentration | 3 | % | 3%-6%
Thickened sludge flow rate | 83.3333 | gpm
DAF Total solids loading | 1250 | lb/hr
Air to solids ratio (lbs. air/lbs. solids | 0.02 | lb/lb | 0.02-0.04
Recycle flow rate | 603.8647 | gpm | (Assuming 0.69 lb air/1000 gal recycle)
Estimated pump kW | 27.5108 | kW | (0.6 efficiency, 175' of head)
Estimated Air Compressor kW | 2.7511
Minimum DAF Diameter | 28 | ft | (Assuming 2.0 gpm/ft^2 rise rate)
Rough installed DAF cost | 420000 | $ | For estimate, contact info@westech-inc.com
Daily Cost of Natural gas without DAF | 420.2814 | $/Day
Annualized cost of natural gas without DAF | 153402.6988 | $/year
Daily Cost of Natural gas WITH DAF | 70.0469 | $/Day
Daily Cost of Electricity With DAF | 112.5428 | $/Day
Annualized total energy costs With DAF | 66645.2261 | $/year
Yearly Cost Savings | 86757.4727 | $/year
Payback Period | 4.8411 | years
ROI on 20 year investment | 1315149.4546 | $